## Input_Holding
simple Measurement table
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark | Table 1. internal STATUS
0 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
1 |  |  | temperature | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C | SEQ Error | ZCT | reserved | T Sag | S Sag | R Sag | T Swell | S Swell | R Swell
2 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz | 0: Normal 1: Reverse | COM state |  | 0 - not occur 1 - occur |  |  | 0 - not occur 1 - occur
3 |  |  | program version |  | 4 | 2 | UINT16 | 1 | V1.01=>0x0101 |  | N(0), A(1)
4 |  |  | present CO2 use(month) | Kg | 4 | 2 | UINT16 | 10 | feeder #1 kWH use, ex) 123 -> 12.3Kg
5 |  |  | reserved |  | 4 | 6
8 | status |  | internal status |  | 4 | 2 | UINT16 | 1 | See Table 1 | Table 2. Feeder status
9 |  |  | feeder #1 status |  | 4 | 2 | UINT16 | 1 | See Table 2 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
10 |  |  | feeder #2 status |  | 4 | 2 | UINT16 | 1 | [13 empty] | T OC | S OC | R OC | operate
11 |  |  | feeder #3 status |  | 4 | 2 | UINT16 | 1 | [13 empty] | 0 - not occur 1 - occur |  |  | 0 - not use 1 - use
12 |  |  | feeder #4 status |  | 4 | 2 | UINT16 | 1
13 |  |  | feeder #5 status |  | 4 | 2 | UINT16 | 1
14 |  |  | feeder #6 status |  | 4 | 2 | UINT16 | 1
15 |  |  | feeder #7 status |  | 4 | 2 | UINT16 | 1
16 |  |  | feeder #8 status |  | 4 | 2 | UINT16 | 1
17 |  |  | feeder #9 status |  | 4 | 2 | UINT16 | 1
18 |  |  | feeder #10 status |  | 4 | 2 | UINT16 | 1
19 |  |  | feeder #11 status |  | 4 | 2 | UINT16 | 1
20 |  |  | feeder #12 status |  | 4 | 2 | UINT16 | 1
21 |  |  | reserved |  | 4 | 86 | UINT16 | 1
64 | voltage | total | V123(LN) average | V | 4 | 4 | UINT32 | 100 | ex) 21543 -> 215.43V
66 |  |  | V123(LL) average | V | 4 | 4 | UINT32 | 100
68 |  |  | V123(LN) unbalance | % | 4 | 2 | UINT16 | 100 | ex) 0123 -> 1.23%
69 |  |  | V123(LL) unbalance | % | 4 | 2 | UINT16 | 100
70 |  | 1 | V1 | V | 4 | 4 | UINT32 | 100
72 |  |  | V12 | V | 4 | 4 | UINT32 | 100
74 |  |  | V1 unbalance | % | 4 | 2 | UINT16 | 100
75 |  |  | V12 unbalance | % | 4 | 2 | UINT16 | 100
76 |  | 2 | V2 | V | 4 | 4 | UINT32 | 100
78 |  |  | V23 | V | 4 | 4 | UINT32 | 100
80 |  |  | V2 unbalance | % | 4 | 2 | UINT16 | 100
81 |  |  | V23 unbalance | % | 4 | 2 | UINT16 | 100
82 |  | 3 | V3 | V | 4 | 4 | UINT32 | 100
84 |  |  | V31 | V | 4 | 4 | UINT32 | 100
86 |  |  | V3 unbalance | % | 4 | 2 | UINT16 | 100
87 |  |  | V31 unbalance | % | 4 | 2 | UINT16 | 100
88 |  |  | reserved |  | 4 | 8 | UINT16 | 100
92 | sag |  | year | year | 4 | 2 | UINT16
93 |  |  | mon | mon | 4 | 2 | UINT16
94 |  |  | day | day | 4 | 2 | UINT16
95 |  |  | hour | hour | 4 | 2 | UINT16
96 |  |  | min | min | 4 | 2 | UINT16
97 |  |  | sec | sec | 4 | 2 | UINT16
98 | swell |  | year | year | 4 | 2 | UINT16
99 |  |  | mon | mon | 4 | 2 | UINT16
100 |  |  | day | day | 4 | 2 | UINT16
101 |  |  | hour | hour | 4 | 2 | UINT16
102 |  |  | min | min | 4 | 2 | UINT16
103 |  |  | sec | sec | 4 | 2 | UINT16
104 |  |  | Va-Va Phase |  | 4 | 2
105 |  |  | Va-Vb Phase |  | 4 | 2
106 |  |  | Va-Vc Phase |  | 4 | 2
107 |  |  | reserved |  | 4 | 26
120 | #1 | total | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P2W_R(1P3W_RN), 2:1P2W_S(1P3W_RS), 3:1P2W_T(1P3WSN), 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W_2CT
121 |  |  | a leakage current | mA | 4 | 2 | UINT16 | 1 | bit15: COM state, bit[14..]: remote leakage current
122 |  |  | current | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A
124 |  |  | W | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
126 |  |  | VAR | VAR | 4 | 4 | INT32 | 1
128 |  |  | VA | VA | 4 | 4 | UINT32 | 1
130 |  |  | PF average | % | 4 | 2 | INT16 | 100 | ex)9870 -> 98.7%
131 |  |  | reserved |  | 4 | 2
132 |  |  | current unbalance | % | 4 | 2 | UINT16 | 100 | ex)012 -> 0.12%
133 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
134 |  |  | reserved |  | 4 | 4 | UINT16 | 100
136 |  | 1 | I1 | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A
138 |  |  | W | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
140 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100 | ex) 012 -> 0.12︒
141 |  |  | power Factor | % | 4 | 2 | INT16 | 100 | ex)9870 -> 98.7%
142 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
143 |  |  | reserved |  | 4 | 2 | UINT16 | 1
144 |  | 2 | I2 | A | 4 | 4 | UINT32 | 100
146 |  |  | W | W | 4 | 4 | INT32 | 1
148 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100
149 |  |  | power Factor | % | 4 | 2 | INT16 | 100
150 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
151 |  |  | reserved |  | 4 | 2 | UINT16 | 1
152 |  | 3 | I3 | A | 4 | 4 | UINT32 | 100
154 |  |  | W | W | 4 | 4 | INT32 | 1
156 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100
157 |  |  | power Factor | % | 4 | 2 | INT16 | 100
158 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
159 |  |  | reserved |  | 4 | 2 | UINT16 | 1
160 | #2 |  |  |  |  | 80
200 | #3 |  |  |  |  | 80
240 | #4 |  |  |  |  | 80
280 | #5 |  |  |  |  | 80
320 | #6 |  |  |  |  | 80
360 | #7 |  |  |  |  | 80
400 | #8 |  |  |  |  | 80
440 | #9 |  |  |  |  | 80
480 | #10 |  |  |  |  | 80
520 | #11 |  |  |  |  | 80
560 | #12 |  |  |  |  | 80
All Measurement table | [9 empty] | V2.15
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
2300 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms
2301 |  |  | temperature 1 | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C
2302 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz
2303 |  |  | program version |  | 4 | 2 | UINT16 | 1 | V1.01=>0x0101
2304 |  |  | present CO2 use(month) | Kg | 4 | 2 | UINT16 | 10 | feeder #1 kWH use, ex) 123 -> 12.3Kg
2305 |  |  | reserved |  | 4 | 6
2308 | status |  | internal status |  | 4 | 2 | UINT16 | 1 | See Table 1
2309 |  |  | feeder #1 status |  | 4 | 2 | UINT16 | 1 | See Table 2
2310 |  |  | feeder #2 status |  | 4 | 2 | UINT16 | 1
2311 |  |  | feeder #3 status |  | 4 | 2 | UINT16 | 1
2312 |  |  | feeder #4 status |  | 4 | 2 | UINT16 | 1
2313 |  |  | feeder #5 status |  | 4 | 2 | UINT16 | 1
2314 |  |  | feeder #6 status |  | 4 | 2 | UINT16 | 1
2315 |  |  | feeder #7 status |  | 4 | 2 | UINT16 | 1
2316 |  |  | feeder #8 status |  | 4 | 2 | UINT16 | 1
2317 |  |  | feeder #9 status |  | 4 | 2 | UINT16 | 1
2318 |  |  | feeder #10 status |  | 4 | 2 | UINT16 | 1
2319 |  |  | feeder #11 status |  | 4 | 2 | UINT16 | 1
2320 |  |  | feeder #12 status |  | 4 | 2 | UINT16 | 1
2321 |  |  | reserved |  | 4 | 86 | UINT16 | 1
2364 | voltage | total | V123(LN) average | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
2366 |  |  | V123(LL) average | V | 4 | 4 | UINT32 | 100
2368 |  |  | V123(LN) unbalance | % | 4 | 2 | UINT16 | 100 | ex)123 -> 1.23%
2369 |  |  | V123(LL) unbalance | % | 4 | 2 | UINT16 | 100
2370 |  | 1 | V1 | V | 4 | 4 | UINT32 | 100
2372 |  |  | V12 | V | 4 | 4 | UINT32 | 100
2374 |  |  | V1 unbalance | % | 4 | 2 | UINT16 | 100
2375 |  |  | V12 unbalance | % | 4 | 2 | UINT16 | 100
2376 |  | 2 | V2 | V | 4 | 4 | UINT32 | 100
2378 |  |  | V23 | V | 4 | 4 | UINT32 | 100
2380 |  |  | V2 unbalance | % | 4 | 2 | UINT16 | 100
2381 |  |  | V23 unbalance | % | 4 | 2 | UINT16 | 100
2382 |  | 3 | V3 | V | 4 | 4 | UINT32 | 100
2384 |  |  | V31 | V | 4 | 4 | UINT32 | 100
2386 |  |  | V3 unbalance | % | 4 | 2 | UINT16 | 100
2387 |  |  | V31 unbalance | % | 4 | 2 | UINT16 | 100
2388 |  |  | reserved |  | 4 | 8
2392 | sag |  | year |  | 4 | 2 | UINT16
2393 |  |  | mon |  | 4 | 2 | UINT16
2394 |  |  | day |  | 4 | 2 | UINT16
2395 |  |  | hour |  | 4 | 2 | UINT16
2396 |  |  | min |  | 4 | 2 | UINT16
2397 |  |  | sec |  | 4 | 2 | UINT16
2398 | swell |  | year |  | 4 | 2 | UINT16
2399 |  |  | mon |  | 4 | 2 | UINT16
2400 |  |  | day |  | 4 | 2 | UINT16
2401 |  |  | hour |  | 4 | 2 | UINT16
2402 |  |  | min |  | 4 | 2 | UINT16
2403 |  |  | sec |  | 4 | 2 | UINT16
2404 | voltage phase angle |  | Va-Va Phase |  | 4 | 2 | UINT16 |  | V2.18 add
2405 |  |  | Va-Vb Phase |  | 4 | 2 | UINT16
2406 |  |  | Va-Vc Phase |  | 4 | 2 | UINT16
2407 |  |  | reserved |  | 4 | 26
2420 | #1 | total | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P_R, 2:1P_S, 3:1P_T, 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W, 9 : ZCT_A,, 10 : ZCT_B, 11: ZCT_C
2421 |  |  | a leakage current | mA | 4 | 2 | UINT16 |  | ext zct module value
2422 |  |  | current | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A, if ZCT used 123->1.23mA
2424 |  |  | W | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
2426 |  |  | VAR | VAR | 4 | 4 | INT32 | 1
2428 |  |  | VA | VA | 4 | 4 | UINT32 | 1
2430 |  |  | PF average | % | 4 | 2 | INT16 | 100 | ex)987 -> 98.7%
2431 |  |  | reserved |  | 4 | 2
2432 |  |  | current unbalance | % | 4 | 2 | UINT16 | 100 | ex)012 -> 0.12%
2433 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
2434 |  |  | reserved | A | 4 | 4 | UINT16 | 1
2436 |  | 1 | V1 | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
2438 |  |  | I1 | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A
2440 |  |  | W | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
2442 |  |  | VAR | VAR | 4 | 4 | INT32 | 1
2444 |  |  | VA | VA | 4 | 4 | UINT32 | 1
2446 |  |  | volt unbalance | % | 4 | 2 | UINT16 | 100 | ex)012 -> 0.12%
2447 |  |  | current unbalance | % | 4 | 2 | UINT16 | 100 | ex)012 -> 0.12%
2448 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100 | ex) 012 -> 0.12︒
2449 |  |  | power factor | % | 4 | 2 | INT16 | 100 | ex)987 -> 98.7%
2450 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
2451 |  |  | reserved |  | 4 | 2 | UINT16 | 1
2452 |  | 2 | V2 | V | 4 | 4 | UINT32 | 100
2454 |  |  | I2 | A | 4 | 4 | UINT32 | 100
2456 |  |  | W | W | 4 | 4 | INT32 | 1
2458 |  |  | VAR | VAR | 4 | 4 | INT32 | 1
2460 |  |  | VA | VA | 4 | 4 | UINT32 | 1
2462 |  |  | volt unbalance | % | 4 | 2 | UINT16 | 100
2463 |  |  | current unbalance | % | 4 | 2 | UINT16 | 100
2464 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100
2465 |  |  | power factor | % | 4 | 2 | INT16 | 100
2466 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
2467 |  |  | reserved |  | 4 | 2 | UINT16 | 1
2468 |  | 3 | V3 | V | 4 | 4 | UINT32 | 100
2470 |  |  | I3 | A | 4 | 4 | UINT32 | 100
2472 |  |  | W | W | 4 | 4 | INT32 | 1
2474 |  |  | VAR | VAR | 4 | 4 | INT32 | 1
2476 |  |  | VA | VA | 4 | 4 | UINT32 | 1
2478 |  |  | volt unbalance | % | 4 | 2 | UINT16 | 100
2479 |  |  | current unbalance | % | 4 | 2 | UINT16 | 100
2480 |  |  | phase | ︒ | 4 | 2 | UINT16 | 100
2481 |  |  | power factor | % | 4 | 2 | INT16 | 100
2482 |  |  | Power THD | % | 4 | 2 | UINT16 | 100
2483 |  |  | reserved |  | 4 | 2 | UINT16 | 1
2484 | #2 |  |  |  |  | 128
2548 | #3 |  |  |  |  | 128
2612 | #4 |  |  |  |  | 128
2676 | #5 |  |  |  |  | 128
2740 | #6 |  |  |  |  | 128
2804 | #7 |  |  |  |  | 128
2868 | #8 |  |  |  |  | 128
2932 | #9 |  |  |  |  | 128
2996 | #10 |  |  |  |  | 128
3060 | #11 |  |  |  |  | 128
3124 | #12 |  |  |  |  | 128
Demand Table
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
5920 | voltage | 1 | V1 Average | V | 4 | 4 | UINT32 | 100 | Current Data
5922 |  |  | V1 Min | V | 4 | 4 | UINT32 | 100
5924 |  |  | V1 Max | V | 4 | 4 | UINT32 | 100
5926 |  | 2 | V2 Average | V | 4 | 4 | UINT32 | 100
5928 |  |  | V2 Min | V | 4 | 4 | UINT32 | 100
5930 |  |  | V2 Max | V | 4 | 4 | UINT32 | 100
5932 |  | 3 | V3 Average | V | 4 | 4 | UINT32 | 100
5934 |  |  | V3 Min | V | 4 | 4 | UINT32 | 100
5936 |  |  | V3 Max | V | 4 | 4 | UINT32 | 100
5938 |  | 1-2 | V1-2 Average | V | 4 | 4 | UINT32 | 100
5940 |  |  | V1-2 Min | V | 4 | 4 | UINT32 | 100
5942 |  |  | V1-2 Max | V | 4 | 4 | UINT32 | 100
5944 |  | 2-3 | V2-3 Average | V | 4 | 4 | UINT32 | 100
5946 |  |  | V2-3 Min | V | 4 | 4 | UINT32 | 100
5948 |  |  | V2-3 Max | V | 4 | 4 | UINT32 | 100
5950 |  | 3-1 | V3-1 Average | V | 4 | 4 | UINT32 | 100
5952 |  |  | V3-1 Min | V | 4 | 4 | UINT32 | 100
5954 |  |  | V3-1 Max | V | 4 | 4 | UINT32 | 100
5956 |  |  | reserved |  | 4 | 2
5957 |  |  | reserved |  | 4 | 2 | INT16 | 10
5958 |  |  | reserved |  | 4 | 2 | INT16 | 10
5959 |  |  | reserved |  | 4 | 2 | INT16 | 10
5960 | voltage | 1 | V1 Average | V | 4 | 4 | UINT32 | 100 | Previous Data
5962 |  |  | V1 Min | V | 4 | 4 | UINT32 | 100
5964 |  |  | V1 Max | V | 4 | 4 | UINT32 | 100
5966 |  | 2 | V2 Average | V | 4 | 4 | UINT32 | 100
5968 |  |  | V2 Min | V | 4 | 4 | UINT32 | 100
5970 |  |  | V2 Max | V | 4 | 4 | UINT32 | 100
5972 |  | 3 | V3 Average | V | 4 | 4 | UINT32 | 100
5974 |  |  | V3 Min | V | 4 | 4 | UINT32 | 100
5976 |  |  | V3 Max | V | 4 | 4 | UINT32 | 100
5978 |  | 1-2 | V1-2 Average | V | 4 | 4 | UINT32 | 100
5980 |  |  | V1-2 Min | V | 4 | 4 | UINT32 | 100
5982 |  |  | V1-2 Max | V | 4 | 4 | UINT32 | 100
5984 |  | 2-3 | V2-3 Average | V | 4 | 4 | UINT32 | 100
5986 |  |  | V2-3 Min | V | 4 | 4 | UINT32 | 100
5988 |  |  | V2-3 Max | V | 4 | 4 | UINT32 | 100
5990 |  | 3-1 | V3-1 Average | V | 4 | 4 | UINT32 | 100
5992 |  |  | V3-1 Min | V | 4 | 4 | UINT32 | 100
5994 |  |  | V3-1 Max | V | 4 | 4 | UINT32 | 100
5996 |  |  | reserved |  | 4 | 2
5997 |  |  | reserved |  | 4 | 2 | INT16 | 10
5998 |  |  | reserved |  | 4 | 2 | INT16 | 10
5999 |  |  | reserved |  | 4 | 2 | INT16 | 10
6000 | #1 | 1 | Demand I | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A
6002 |  |  | Max I | A | 4 | 4 | UINT32 | 100
6004 |  |  | Demand W | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
6006 |  |  | Max W | W | 4 | 4 | INT32 | 1
6008 |  | 2 | Demand I | A | 4 | 4 | UINT32 | 100
6010 |  |  | Max I | A | 4 | 4 | UINT32 | 100
6012 |  |  | Demand W | W | 4 | 4 | INT32 | 1
6014 |  |  | Max W | W | 4 | 4 | INT32 | 1
6016 |  | 3 | Demand I | A | 4 | 4 | UINT32 | 100
6018 |  |  | Max I | A | 4 | 4 | UINT32 | 100
6020 |  |  | Demand W | W | 4 | 4 | INT32 | 1
6022 |  |  | Max W | W | 4 | 4 | INT32 | 1
6024 |  | totoal | Demand total I | A | 4 | 4 | UINT32 | 100
6026 |  |  | Demand total Max I | A | 4 | 4 | UINT32 | 100
6028 |  |  | Demand total W | W | 4 | 4 | INT32 | 1
6030 |  |  | Demand total Max W | W | 4 | 4 | INT32 | 1
6032 |  |  | Demand total W prediction | W | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
6034 | #2 |  |  |  |  | 68
6068 | #3 |  |  |  |  | 68
6102 | #4 |  |  |  |  | 68
6136 | #5 |  |  |  |  | 68
6170 | #6 |  |  |  |  | 68
6204 | #7 |  |  |  |  | 68
6238 | #8 |  |  |  |  | 68
6272 | #9 |  |  |  |  | 68
6306 | #10 |  |  |  |  | 68
6340 | #11 |  |  |  |  | 68
6374 | #12 |  |  |  |  | 68
Received KWh table
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
8000 | #1 | KWh | sum |  | 4 | 4 | UINT32 | 10 | kWH. Ex)101 -> 10.1kWH
8002 |  |  | this month |  | 4 | 4 | UINT32 | 10
8004 |  |  | last month |  | 4 | 4 | UINT32 | 10
8006 |  | KVARh | sum |  | 4 | 4 | UINT32 | 10
8008 |  |  | this month |  | 4 | 4 | UINT32 | 10
8010 |  |  | last month |  | 4 | 4 | UINT32 | 10
8012 |  | KVAh | sum |  | 4 | 4 | UINT32 | 10
8014 |  |  | this month |  | 4 | 4 | UINT32 | 10
8016 |  |  | last month |  | 4 | 4 | UINT32 | 10
8018 | #2 |  |  |  |  | 36
8036 | #3 |  |  |  |  | 36 |  |  |  | 2392
8054 | #4 |  |  |  |  | 36
8072 | #5 |  |  |  |  | 36
8090 | #6 |  |  |  |  | 36
8108 | #7 |  |  |  |  | 36
8126 | #8 |  |  |  |  | 36
8144 | #9 |  |  |  |  | 36
8162 | #10 |  |  |  |  | 36
8180 | #11 |  |  |  |  | 36
8198 | #12 |  |  |  |  | 36
ALL 1P2W
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
9000 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms
9001 |  |  | temperature 1 | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C
9002 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz
9003 |  |  | reserved |  | 4 | 14
9010 |  |  | V | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
9012 | #1 |  | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P_R, 2:1P_S, 3:1P_T, 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W, 9 : ZCT_A,, 10 : ZCT_B, 11: ZCT_C
9013 |  |  | reserved |  | 4 | 2 | UINT16 | 1
9014 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9016 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123W, if ZCT used 12.3mA
9018 |  |  | VAR/Igc | VAR | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123Var, if ZCT used 12.3mA
9020 |  |  | VA/unused | VA | 4 | 4 | UINT32 | 1
9022 |  |  | power factor/unused | % | 4 | 2 | INT16 | 100 | ex)987 -> 98.7%
9023 |  |  | phase | % | 4 | 2 | UINT16 | 100 | ex)123 -> 1.23%
9024 |  |  | kWh/unused | kWh | 4 | 4 | UINT32 | 10 | kWH. Ex)101 -> 10.1kWH
9026 |  |  | kVarh/unused | kVarh | 4 | 4 | UINT32 | 10
9028 |  |  | reserved |  | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
9030 | #2 |  |  |  |  | 36
9048 | #3 |  |  |  |  | 36
9066 | #4 |  |  |  |  | 36
9084 | #5 |  |  |  |  | 36
9102 | #6 |  |  |  |  | 36
9120 | #7 |  |  |  |  | 36
9138 | #8 |  |  |  |  | 36
9156 | #9 |  |  |  |  | 36
9174 | #10 |  |  |  |  | 36
9192 | #11 |  |  |  |  | 36
9210 | #12 |  |  |  |  | 36
ZCT TYPE
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
9300 | #1 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9301 | #2 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9302 | #3 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9303 | #4 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9304 | #5 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9305 | #6 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9306 | #7 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9307 | #8 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9308 | #9 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9309 | #10 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9310 | #11 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9311 | #12 |  | I/Ig | A | 4 | 2 | UINT16 | 10 | ex) 123 -> 1.23A, if ZCT used 1.23mA
compact map(3512S)
addr | item | phase | descrpition | Unit | FC | size | type | scale | Remark
9900 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms
9901 |  |  | temperature 1 | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C
9902 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz
9903 |  |  | V | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
9905 | #1 |  | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P_R, 2:1P_S, 3:1P_T, 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W, 9 : ZCT_A,, 10 : ZCT_B, 11: ZCT_C
9906 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A, if ZCT used 1.23mA
9908 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123W, if ZCT used 12.3mA
9910 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
9912 | #2 |  |  |  | 4 | 14
9919 | #3 |  |  |  | 4 | 14
9926 | #4 |  |  |  | 4 | 14
9933 | #5 |  |  |  | 4 | 14
9940 | #6 |  |  |  | 4 | 14
9947 | #7 |  |  |  | 4 | 14
9954 | #8 |  |  |  | 4 | 14
9961 | #9 |  |  |  | 4 | 14
9968 | #10 |  |  |  | 4 | 14
9975 | #11 |  |  |  | 4 | 14
9982 | #12 |  |  |  | 4 | 14
Time
addr | 항목 | phase | 설명 | Unit | FC | size | type | scale | 비고
0 | lock |  | write time set enable |  | 3,16 | 2 | UINT16 | 1 | 0x1234 : unlock, 0 : lock
1 | Time |  | year |  | 3,16 | 2 | UINT16 | 1 | 2012
2 |  |  | month |  | 3,16 | 2 | UINT16 | 1 | 1~12
3 |  |  | day |  | 3,16 | 2 | UINT16 | 1 | 1~31
4 |  |  | weekdays |  | 3,16 | 2 | UINT16 | 1 | 0 : sun, 1 : mon
5 |  |  | hour |  | 3,16 | 2 | UINT16 | 1 | 0~23
6 |  |  | min |  | 3,16 | 2 | UINT16 | 1 | 0~59
7 |  |  | sec |  | 3,16 | 2 | UINT16 | 1 | 0~59
120 | Demand |  | Demand Reset |  | 3,16 | 2 | UINT16 | 1 | 0x1234 : reset
GEMS3500 ENERGY
addr | 항목 | phase | 설명 |  | FC | size | type | scale | 비고
10000 | #1 | KWh | import |  | 4 | 4 | UINT32 | 10
10002 |  |  | export |  | 4 | 4 | UINT32 | 10
10004 |  | kvarh | import |  | 4 | 4 | UINT32 | 10
10006 |  |  | export |  | 4 | 4 | UINT32 | 10
10008 |  | kVAh |  |  | 4 | 4 | UINT32 | 10
10010 | #2 |  |  |  | 4 | 20
10020 | #3 |  |  |  | 4 | 20
10030 | #4 |  |  |  | 4 | 20
10040 | #5 |  |  |  | 4 | 20
10050 | #6 |  |  |  | 4 | 20
10060 | #7 |  |  |  | 4 | 20
10070 | #8 |  |  |  | 4 | 20
10080 | #9 |  |  |  | 4 | 20
10090 | #10 |  |  |  | 4 | 20
10100 | #11 |  |  |  | 4 | 20
10110 | #12 |  |  |  | 4 | 20
10120 | #13 |  |  |  | 4 | 20
10130 | #14 |  |  |  | 4 | 20
10140 | #15 |  |  |  | 4 | 20
10150 | #16 |  |  |  | 4 | 20
10160 | #17 |  |  |  | 4 | 20
10170 | #18 |  |  |  | 4 | 20
10180 | #19 |  |  |  | 4 | 20
10190 | #20 |  |  |  | 4 | 20
10200 | #21 |  |  |  | 4 | 20
10210 | #22 |  |  |  | 4 | 20
10220 | #23 |  |  |  | 4 | 20
10230 | #24 |  |  |  | 4 | 20
10240 | #25 |  |  |  | 4 | 20
10250 | #26 |  |  |  | 4 | 20
10260 | #27 |  |  |  | 4 | 20
10270 | #28 |  |  |  | 4 | 20
10280 | #29 |  |  |  | 4 | 20
10290 | #30 |  |  |  | 4 | 20
10300 | #31 |  |  |  | 4 | 20
10310 | #32 |  |  |  | 4 | 20
10320 | #33 |  |  |  | 4 | 20
10330 | #34 |  |  |  | 4 | 20
10340 | #35 |  |  |  | 4 | 20
10350 | #36 |  |  |  | 4 | 20
10360 | #37 |  |  |  | 4 | 20
10370 | #38 |  |  |  | 4 | 20
10380 | #39 |  |  |  | 4 | 20
10390 | #40 |  |  |  | 4 | 20
10400 | #41 |  |  |  | 4 | 20
10410 | #42 |  |  |  | 4 | 20
10420 | #43 |  |  |  | 4 | 20
10430 | #44 |  |  |  | 4 | 20
10440 | #45 |  |  |  | 4 | 20
10450 | #46 |  |  |  | 4 | 20
10460 | #47 |  |  |  | 4 | 20
10470 | #48 |  |  |  | 4 | 20
10480 | #49 |  |  |  | 4 | 20
10490 | #50 |  |  |  | 4 | 20
10500 | #51 |  |  |  | 4 | 20
10510 | #52 |  |  |  | 4 | 20
10520 | #53 |  |  |  | 4 | 20
10530 | #54 |  |  |  | 4 | 20
gems3512 : ALL 1P2W
[10 empty] | addr | 번호 | 항목 | phase | 설명 |  | FC | size | type | scale | 비고
[10 empty] | 9000 | 1 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms
[10 empty] | 9001 | 2 |  |  | temperature 1 | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C
[10 empty] | 9002 | 3 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz
[10 empty] | 9003 | 4 |  |  | reserved |  | 4 | 14
[10 empty] | 9010 | 5 |  |  | V | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
[10 empty] | 9012 | 6 | #1 |  | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P_R, 2:1P_S, 3:1P_T, 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W, 9 : ZCT_A,, 10 : ZCT_B, 11: ZCT_C
[10 empty] | 9013 | 7 |  |  | reserved |  | 4 | 2 | UINT16 | 1
[10 empty] | 9014 | 8 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A, if ZCT used 1.23mA
[10 empty] | 9016 | 9 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123W, if ZCT used 12.3mA
[10 empty] | 9018 | 10 |  |  | VAR/Igc | VAR | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123Var, if ZCT used 12.3mA
[10 empty] | 9020 | 11 |  |  | VA/unused | VA | 4 | 4 | UINT32 | 1
[10 empty] | 9022 | 12 |  |  | power factor/unused | % | 4 | 2 | INT16 | 100 | ex)987 -> 98.7%
[10 empty] | 9023 | 13 |  |  | phase | % | 4 | 2 | UINT16 | 100 | ex)123 -> 1.23%
[10 empty] | 9024 | 14 |  |  | kWh/unused | kWh | 4 | 4 | UINT32 | 10 | kWH. Ex)101 -> 10.1kWH
[10 empty] | 9026 | 15 |  |  | kVarh/unused | kVarh | 4 | 4 | UINT32 | 10
[10 empty] | 9028 | 16 |  |  | reserved |  | 4 | 4 | INT32 | 1 | ex) 123 -> 123W
[10 empty] | 9030 |  | #2 |  |  |  |  | 36
[10 empty] | 9048 |  | #3 |  |  |  |  | 36
[10 empty] | 9066 |  | #4 |  |  |  |  | 36
[10 empty] | 9084 |  | #5 |  |  |  |  | 36
[10 empty] | 9102 |  | #6 |  |  |  |  | 36
[10 empty] | 9120 |  | #7 |  |  |  |  | 36
[10 empty] | 9138 |  | #8 |  |  |  |  | 36
[10 empty] | 9156 |  | #9 |  |  |  |  | 36
[10 empty] | 9174 |  | #10 |  |  |  |  | 36
[10 empty] | 9192 |  | #11 |  |  |  |  | 36
[10 empty] | 9210 |  | #12 |  |  |  |  | 36
compact map(3512S에만 적용)
[10 empty] | addr | 번호 | 항목 | phase | 설명 |  | FC | size | type | scale | 비고
[10 empty] | 9900 | 1 | system |  | operation Heartbit |  | 4 | 2 | UINT16 | 1 | increase per 100ms
[10 empty] | 9901 | 2 |  |  | temperature 1 | ︒C | 4 | 2 | INT16 | 10 | ex) 350 -> 35.0︒C
[10 empty] | 9902 | 3 |  |  | frequency | Hz | 4 | 2 | UINT16 | 100 | ex) 6012 -> 60.12Hz
[10 empty] | 9903 | 4 |  |  | V | V | 4 | 4 | UINT32 | 100 | ex) 21412 -> 214.12V
[10 empty] | 9905 | 5 | #1 |  | type |  | 4 | 2 | UINT16 | 1 | 0:not used, 1:1P_R, 2:1P_S, 3:1P_T, 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W, 9 : ZCT_A,, 10 : ZCT_B, 11: ZCT_C
[10 empty] | 9906 | 6 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100 | ex) 123 -> 1.23A, if ZCT used 1.23mA
[10 empty] | 9908 | 7 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10 | ex) 123 -> 123W, if ZCT used 12.3mA
[10 empty] | 9910 | 8 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9912 | 9 | #2 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9913 | 10 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9915 | 11 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9917 | 12 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9919 | 13 | #3 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9920 | 14 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9922 | 15 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9924 | 16 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9926 | 17 | #4 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9927 | 18 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9929 | 19 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9931 | 20 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9933 | 21 | #5 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9934 | 22 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9936 | 23 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9938 | 24 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9940 | 25 | #6 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9941 | 26 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9943 | 27 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9945 | 28 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9947 | 29 | #7 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9948 | 30 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9950 | 31 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9952 | 32 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9954 | 33 | #8 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9955 | 34 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9957 | 35 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9959 | 36 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9961 | 37 | #9 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9962 | 38 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9964 | 39 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9966 | 40 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9968 | 41 | #10 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9969 | 42 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9971 | 43 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9973 | 44 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9975 | 45 | #11 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9976 | 46 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9978 | 47 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9980 | 48 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[10 empty] | 9982 | 49 | #12 |  | type |  | 4 | 2 | UINT16 | 1
[10 empty] | 9983 | 50 |  |  | I/Ig | A | 4 | 4 | UINT32 | 100
[10 empty] | 9985 | 51 |  |  | W/Igr | W | 4 | 4 | INT32 | 1¦10
[10 empty] | 9987 | 52 |  |  | kwh | kwh | 4 | 4 | UINT32 | 10
[21 empty] | 4 | 3 | 2 | 1 | 0
Table 2. ZCT
[10 empty] | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5
[10 empty] | OC | Value(0 ~ 10000)

## Energy
Received KWh table
addr | item | phase | descrpition | Unit | FC | size | type | scale
2002 | #1 | KWh | sum | 3 | 4 | UINT32 | 10 | kWH. Ex)101 -> 10.1kWH
2004 |  |  | this month | 3 | 4 | UINT32 | 10
2006 |  |  | last month | 3 | 4 | UINT32 | 10
2008 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2010 |  |  | this month | 3 | 4 | UINT32 | 10
2012 |  |  | last month | 3 | 4 | UINT32 | 10
2014 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2016 |  |  | this month | 3 | 4 | UINT32 | 10
2018 |  |  | last month | 3 | 4 | UINT32 | 10
2020 | #2 | KWh | sum | 3 | 4 | UINT32 | 10
2022 |  |  | this month | 3 | 4 | UINT32 | 10
2024 |  |  | last month | 3 | 4 | UINT32 | 10
2026 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2028 |  |  | this month | 3 | 4 | UINT32 | 10
2030 |  |  | last month | 3 | 4 | UINT32 | 10
2032 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2034 |  |  | this month | 3 | 4 | UINT32 | 10
2036 |  |  | last month | 3 | 4 | UINT32 | 10
2038 | #3 | KWh | sum | 3 | 4 | UINT32 | 10
2040 |  |  | this month | 3 | 4 | UINT32 | 10
2042 |  |  | last month | 3 | 4 | UINT32 | 10
2044 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2046 |  |  | this month | 3 | 4 | UINT32 | 10
2048 |  |  | last month | 3 | 4 | UINT32 | 10
2050 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2052 |  |  | this month | 3 | 4 | UINT32 | 10
2054 |  |  | last month | 3 | 4 | UINT32 | 10
2056 | #4 | KWh | sum | 3 | 4 | UINT32 | 10
2058 |  |  | this month | 3 | 4 | UINT32 | 10
2060 |  |  | last month | 3 | 4 | UINT32 | 10
2062 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2064 |  |  | this month | 3 | 4 | UINT32 | 10
2066 |  |  | last month | 3 | 4 | UINT32 | 10
2068 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2070 |  |  | this month | 3 | 4 | UINT32 | 10
2072 |  |  | last month | 3 | 4 | UINT32 | 10
2074 | #5 | KWh | sum | 3 | 4 | UINT32 | 10
2076 |  |  | this month | 3 | 4 | UINT32 | 10
2078 |  |  | last month | 3 | 4 | UINT32 | 10
2080 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2082 |  |  | this month | 3 | 4 | UINT32 | 10
2084 |  |  | last month | 3 | 4 | UINT32 | 10
2086 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2088 |  |  | this month | 3 | 4 | UINT32 | 10
2090 |  |  | last month | 3 | 4 | UINT32 | 10
2092 | #6 | KWh | sum | 3 | 4 | UINT32 | 10
2094 |  |  | this month | 3 | 4 | UINT32 | 10
2096 |  |  | last month | 3 | 4 | UINT32 | 10
2098 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2100 |  |  | this month | 3 | 4 | UINT32 | 10
2102 |  |  | last month | 3 | 4 | UINT32 | 10
2104 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2106 |  |  | this month | 3 | 4 | UINT32 | 10
2108 |  |  | last month | 3 | 4 | UINT32 | 10
2110 | #7 | KWh | sum | 3 | 4 | UINT32 | 10
2112 |  |  | this month | 3 | 4 | UINT32 | 10
2114 |  |  | last month | 3 | 4 | UINT32 | 10
2116 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2118 |  |  | this month | 3 | 4 | UINT32 | 10
2120 |  |  | last month | 3 | 4 | UINT32 | 10
2122 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2124 |  |  | this month | 3 | 4 | UINT32 | 10
2126 |  |  | last month | 3 | 4 | UINT32 | 10
2128 | #8 | KWh | sum | 3 | 4 | UINT32 | 10
2130 |  |  | this month | 3 | 4 | UINT32 | 10
2132 |  |  | last month | 3 | 4 | UINT32 | 10
2134 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2136 |  |  | this month | 3 | 4 | UINT32 | 10
2138 |  |  | last month | 3 | 4 | UINT32 | 10
2140 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2142 |  |  | this month | 3 | 4 | UINT32 | 10
2144 |  |  | last month | 3 | 4 | UINT32 | 10
2146 | #9 | KWh | sum | 3 | 4 | UINT32 | 10
2148 |  |  | this month | 3 | 4 | UINT32 | 10
2150 |  |  | last month | 3 | 4 | UINT32 | 10
2152 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2154 |  |  | this month | 3 | 4 | UINT32 | 10
2156 |  |  | last month | 3 | 4 | UINT32 | 10
2158 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2160 |  |  | this month | 3 | 4 | UINT32 | 10
2162 |  |  | last month | 3 | 4 | UINT32 | 10
2164 | #10 | KWh | sum | 3 | 4 | UINT32 | 10
2166 |  |  | this month | 3 | 4 | UINT32 | 10
2168 |  |  | last month | 3 | 4 | UINT32 | 10
2170 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2172 |  |  | this month | 3 | 4 | UINT32 | 10
2174 |  |  | last month | 3 | 4 | UINT32 | 10
2176 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2178 |  |  | this month | 3 | 4 | UINT32 | 10
2180 |  |  | last month | 3 | 4 | UINT32 | 10
2182 | #11 | KWh | sum | 3 | 4 | UINT32 | 10
2184 |  |  | this month | 3 | 4 | UINT32 | 10
2186 |  |  | last month | 3 | 4 | UINT32 | 10
2188 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2190 |  |  | this month | 3 | 4 | UINT32 | 10
2192 |  |  | last month | 3 | 4 | UINT32 | 10
2194 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2196 |  |  | this month | 3 | 4 | UINT32 | 10
2198 |  |  | last month | 3 | 4 | UINT32 | 10
2200 | #12 | KWh | sum | 3 | 4 | UINT32 | 10
2202 |  |  | this month | 3 | 4 | UINT32 | 10
2204 |  |  | last month | 3 | 4 | UINT32 | 10
2206 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2208 |  |  | this month | 3 | 4 | UINT32 | 10
2210 |  |  | last month | 3 | 4 | UINT32 | 10
2212 |  | KVAh | sum | 3 | 4 | UINT32 | 10
2214 |  |  | this month | 3 | 4 | UINT32 | 10
2216 |  |  | last month | 3 | 4 | UINT32 | 10
2974 | WH Save |  |  | 3 | 4 | UINT32 | 1 | setting : 0x1234, normal : 0
Export Energy table
addr | item | phase | descrpition | Unit | FC | size | type | scale
2978 | #1 | KWh | sum | 3 | 4 | UINT32 | 10 | kWH. Ex)101 -> 10.1kWH
2980 |  |  | this month | 3 | 4 | UINT32 | 10
2982 |  |  | last month | 3 | 4 | UINT32 | 10
2984 |  | KVARh | sum | 3 | 4 | UINT32 | 10
2986 |  |  | this month | 3 | 4 | UINT32 | 10
2988 |  |  | last month | 3 | 4 | UINT32 | 10
2990 | #2 |  |  | 3 | 24
3002 | #3 |  |  | 3 | 24
3014 | #4 |  |  | 3 | 24
3026 | #5 |  |  | 3 | 24
3038 | #6 |  |  | 3 | 24
3050 | #7 |  |  | 3 | 24
3062 | #8 |  |  | 3 | 24
3074 | #9 |  |  | 3 | 24
3086 | #10 |  |  | 3 | 24
3098 | #11 |  |  | 3 | 24
3110 | #12 |  |  | 3 | 24

## setting
addr | item |  | descrpition | FC | size | type | scale | default | Remark
0 | Time | write time set enable |  | 3,16 | 2 | UINT16 | 10 |  | 0x1234 : unlock, 0 : lock
1 |  | year |  | 3,16 | 2 | UINT16 | 10 | 2012 | 2012
2 |  | month |  | 3,16 | 2 | UINT16 | 10 | 1~12 | 1~12
3 |  | day |  | 3,16 | 2 | UINT16 | 10 | 1~31 | 1~31
4 |  | weekdays |  | 3,16 | 2 | UINT16 | 10 |  | 0 : sun, 1 : mon
5 |  | hour |  | 3,16 | 2 | UINT16 | 10 | 0~23 | 0~23
6 |  | min |  | 3,16 | 2 | UINT16 | 10 | 0~59 | 0~59
7 |  | sec |  | 3,16 | 2 | UINT16 | 10 | 0~59 | 0~59
8 |  | reserved |  | 3,16 | 4
10 | Cloud | cloud domain name1 |  | 3,16 | 40 | UINT16 | 1 |  | V2.18
30 |  | cloud domain name2 |  | 3,16 | 40 | UINT16 | 1 |  | V2.18
50 |  | sntp server domain name |  | 3,16 | 40 | UINT16 | 1 |  | V2.18
70 |  | cloud server2 ip1 |  | 3,16 | 2 | UINT16 | 1 |  | V2.18
71 |  | cloud server2 ip2 |  | 3,16 | 2 | UINT16 | 1 |  | V2.18
72 |  | cloud2 use |  | 3,16 | 2 | UINT16 | 1 |  | V2.18
73 |  | reserved |  | 3,16 | 94 | UINT16 | 1 |  | V2.18
120 | Demand | Demand Reset |  | 3,16 | 2 | UINT16 | 1 |  | 0x1234 : reset
121 | DB | DB write enable |  | 3,16 | 2 |  | 1 |  | 0x1234 : write enable
122 | Config | feeder count |  | 3,16 | 2 | UINT16 | 1 | 18
123 |  | frequency |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : 60Hz, 1 : 50Hz
124 |  | vlotage type |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : 3P4W, 1 : 3P3W, 2 : 1P3W
125 |  | INT. DO |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : not used 1 : temp alarm 2 : event(sag,swell,event) alarm 3 : Demand Alarm 3, 4 : Remote Control
126 |  | INT. DO reset | reset | 3,16 | 2 | UINT16 | 1 | 0 | 0 : status change, 1 : DI, 2: comm
127 |  | EXT. gems3200 count | external gems3200 count | 3,16 | 2 | UINT16 | 1 | 0
128 |  | EXT.ZCT count |  | 3,16 | 2 | UINT16 | 1 | 0
129 |  | PF Sign |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : IEC 1: IEEE
130 |  | VA Type |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : rms, 1 : Vector
131 |  | Data update | data update time(Sec) | 3,16 | 2 | UINT16 | 1 | 0 | 0~65535, 0 : 0.5s, 1 : 1sec
132 |  | channel type |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : 18, 1 : 27, 2 : 36, 3 : 45, 4 : 54
133 |  | noload_Freq | 0 ~ 1000Hz | 3,16 | 2 | UINT16 | 1
134 |  | Noload_Volt | 0 ~ 1000V | 3,16 | 2 | UINT16 | 1
135 |  | Noload_Time |  | 3,16 | 2 | UINT16 | 1
136 | Comm | protocol |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : standard, 1 : nonstandard
137 |  | modbus ID |  | 3,16 | 2 | UINT16 | 1 | 1
138 |  | DEV IP1 |  | 3,16 | 2 | UINT16 | 1 |  | 192.168.7.64
139 |  | DEV IP2 |  | 3,16 | 2 | UINT16 | 1
140 |  | DEV GW1 |  | 3,16 | 2 | UINT16 | 1 |  | 192.168.7.1
141 |  | DEV GW2 |  | 3,16 | 2 | UINT16 | 1
142 |  | DEV SM1 |  | 3,16 | 2 | UINT16 | 1 |  | 255.255.255.0
143 |  | DEV SM2 |  | 3,16 | 2 | UINT16 | 1
144 |  | DEV port |  | 3,16 | 2 | UINT16 | 1 | 502
145 |  | manufacture ID1 |  | 3,16 | 2 | UINT16 | 1
146 |  | manufacture ID2 |  | 3,16 | 2 | UINT16 | 1
147 |  | 485 port | 485 use | 3,16 | 2 | UINT16 | 1 | 0 | 0 : not used, 1 : demand control, 2 : modbus slave, 3 : zct comm
148 |  | 485 baudrate |  | 3,16 | 2 | UINT16 | 1 | 2 | 0 : 9600, 1 : 19200, 2 : 38400, 3 : 57600, 4 : 115200
149 |  | reserved |  | 3,16 | 2 | UINT16 | 1
150 |  | reserved |  | 3,16 | 2 | UINT16 | 1
151 | ETC | ai select |  | 3,16 | 2 | UINT16 | 1 |  | 0 : ntc, 1 : 4~20mA
152 |  | ai min |  | 3,16 | 2 | UINT16 | 1 |  | 4mA : engineering value
153 |  | ai max |  | 3,16 | 2 | UINT16 | 1 |  | 20mA : engineering value
154 |  | reserved |  | 3,16 | 4 | UINT16 | 10
156 |  | Deadband |  | 3,16 | 4 | UINT32 | 10 | 50 | 5%
158 |  | 1st PT ratio |  | 3,16 | 4 | UINT32 | 1 | 220
160 |  | 2nd PT ratio |  | 3,16 | 4 | UINT32 | 1 | 220
162 |  | sag level |  | 3,16 | 4 | UINT32 | 10 | 1800 | 180.0V
164 |  | swell level |  | 3,16 | 4 | UINT32 | 10 | 240 | 240.0V
166 |  | sag period |  | 3,16 | 2 | UINT16 | 1 | 0 | 단위 : half cycle
167 |  | swell period |  | 3,16 | 2 | UINT16 | 1 | 0 | 단위 : half cycle
168 |  | overcurrent delay time |  | 3,16 | 2 | UINT16 | 1 | 5 | step : 1sec
169 |  | SD Memory Read |  | 3,16 | 2 | UINT16 | 1 | 0 | 0x1234 : Read
170 |  | SD Memory Save |  | 3,16 | 2 | UINT16 | 1 | 0 | 0x1234 : Save
171 | Reset | WH clear |  | 3,16 | 2 | UINT16 | 1 | 0 | 0x1234 : reset
172 |  | DO reset |  | 3,16 | 2 | UINT16 | 1 | 0 | 0x1234 : reset
173 |  | Event reset |  | 3,16 | 2 | UINT16 | 1 | 0 | 0x1234 : reset
174 | Demand | Demand Time |  | 3,16 | 2 | UINT16 | 1 | 15 | 15/30/60min
175 |  | alarm 1 level | target demand kW alarm | 3,16 | 2 | UINT16 | 1 | 80 | unit : %
176 |  | alarm 2 level |  | 3,16 | 2 | UINT16 | 1 | 90 | unit : %
177 |  | alarm 3 level |  | 3,16 | 2 | UINT16 | 1 | 100 | unit : %
178 | cloud & WIFI | Input measure |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : use, 1 : not use
179 |  | cloud data format |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : total data send, 1 : ch data send
180 |  | Site ID |  | 3,16 | 4 | UINT32
182 |  | Device ID |  | 3,16 | 4 | UINT32
184 |  | Serial Number |  | 3,16 | 4 | UINT32
186 |  | Sampling Period |  | 3,16 | 4 | UINT32 |  |  | ms
188 |  | SNTP use |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : not used, 1 : used
189 |  | SNTP server IP1_1 |  | 3,16 | 2 | UINT16 | 1 | 0
190 |  | SNTP server IP1_2 |  | 3,16 | 2 | UINT16 | 1 | 0
191 |  | SNTP time zone |  | 3,16 | 2 | INT16 | 1 | 0 | unit : min
192 |  | Cloud1 IP1 |  | 3,16 | 2 | UINT16
193 |  | Cloud1 IP2 |  | 3,16 | 2 | UINT16
194 |  | device name |  | 3,16 | 16 | UINT32
202 |  | WIFI Enable |  | 3,16 | 2 | UINT32 | 1 | 0
203 |  | WIFI DHCP use |  | 3,16 | 2 | UINT16 | 1 | 0
204 |  | WIFI SSID | SSID name | 3,16 | 20 | UINT16 | 1 | 0
214 |  | WIFI Password | WIFI password | 3,16 | 20 | UINT16 | 1 | 0
224 |  | WIFI IP1_1 |  | 3,16 | 2 | UINT16 | 1 | 0
225 |  | WIFI IP1_2 |  | 3,16 | 2 | UINT16 | 1 | 0
226 |  | WIFI GW1_1 |  | 3,16 | 2 | UINT16 | 1 | 0
227 |  | WIFI GW1_2 |  | 3,16 | 2 | UINT16 | 1 | 0
228 |  | WIFI SM1_1 |  | 3,16 | 2 | UINT16 | 1 | 0
229 |  | WIFI SM1_2 |  | 3,16 | 2 | UINT16 | 1 | 0
230 |  | WIFI DNS1_1 |  | 3,16 | 2 | UINT16 | 1 | 0
231 |  | WIFI DNS1_2 |  | 3,16 | 2 | UINT16 | 1 | 0
232 |  | HOST1 Port |  | 3,16 | 2 | UINT16 |  |  | server port(V2.15)
233 |  | HOST2 Port |  | 3,16 | 2 | UINT16 |  |  | V2.18
234 |  | DEV DNS1_1 |  | 3,16 | 2 | UINT16
235 |  | DEV DNS1_2 |  | 3,16 | 2 | UINT16
236 |  | DEV DNS2_1 |  | 3,16 | 2 | UINT16
237 |  | DEV DNS2_2 |  | 3,16 | 2 | UINT16
238 |  | Cloud1 use |  | 3,16 | 2 | UINT16 | 1 | 0 | * cloud server type(V2.15)
239 |  | DHCP use |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : not used, 1 : used
240 | #1 | type | wiring thype | 3,16 | 2 | UINT16 | 1 | 5 | 0:not used, 1:1P2W_R(1P3W_RN), 2:1P2W_S(1P3W_RS), 3:1P2W_T(1P3WSN), 4: 3P3W_2CT, 5 :3P4W, 6 : ZCT, 7 : 3P3W_3CT, 8 : 1P3W_2CT
241 |  | 1st CT ratio(LSW) |  | 3,16 | 2 | UINT16 | 1 | 100 | 1st CT ration LSW(2.17)
242 |  | 2nd CT ratio |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : 100mA, 1 : 5A
243 |  | CT Turn ratio |  | 3,16 | 2 | UINT16 | 1 | 1 | 1~10
244 |  | connected CH #1 | Terminal number | 3,16 | 2 | UINT16 | 1 | 1
245 |  | connected CH #2 |  | 3,16 | 2 | UINT16 | 1 | 2
246 |  | connected CH #3 |  | 3,16 | 2 | UINT16 | 1 | 3
247 |  | starting current |  | 3,16 | 2 | UINT16 | 100 | 1 | 0.01
248 |  | OverCurrnet Level | OC level | 3,16 | 4 | UINT32 | 100 | 8000 | 80A
250 |  | target Demand kW |  | 3,16 | 4 | UINT32 | 1 | 1 | unit : kW
252 |  | demand alarm use |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : not used, 1 : Internal DO use, 2 : External DO use
253 |  | demand control Ext. ID |  | 3,16 | 2 | UINT16 | 1 | 0 | 1~6
254 |  | demand control Ext. point |  | 3,16 | 2 | UINT16 | 1 | 0 | 1~5
255 |  | CT Type |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : Ring CT, 1 : Clamp CT(mA), 2 : Clamp CT(mV), 3: Rogowski
256 |  | CT wire length |  | 3,16 | 2 | UINT16 | 1 | 0 | 0 : 10m, 1: 50m, 2 : 100m
257 |  | 1st CT ratio(MSW) |  | 3,16 | 2 | UINT16 | 1 | 0 | 1st CT ration MSW(2.17)
258 |  | reserved |  | 3,16 | 2 | UINT16 | 1 | 0
259 |  | reserved |  | 3,16 | 2 | UINT16 | 1 | 0
260 | #2 |  |  |  | 40
280 | #3 |  |  |  | 40
300 | #4 |  |  |  | 40
320 | #5 |  |  |  | 40
340 | #6 |  |  |  | 40
360 | #7 |  |  |  | 40
380 | #8 |  |  |  | 40
400 | #9 |  |  |  | 40
420 | #10 |  |  |  | 40
440 | #11 |  |  |  | 40
460 | #12 |  |  |  | 40
1320 |  | DB Save |  | 3,16 | 2 | UINT16 |  |  | setting : 0x1234, normal : 0